Single phase transformer

Working Principle of a transformer

A transformer is a static piece of apparatus by means of which electric power in one circuit is transformed into electric power of the same frequency in another circuit. It can raise or lower voltage in a circuit but with corresponding decrease or increase in current. The physical basis of a transformer is mutual induction between the two circuits linked by a common magnetic flux. In its simplest form, it consists of two inductive coils which are electrically separated but magnetically linked through a path of low reluctance.

∅

Secondary

Primary

∅

Secondary

Primary

If one coil is connected to a source of alternating voltage, an alternating flux is set up in the laminated core, most of which is linked with the other coil which produces mutually induced emf. The coil connected to ac mains is called primary winding while the other from which the energy is drawn from is called secondary winding.

Ideal transformer

An ideal transformer is one which has no copper losses, no iron losses and no magnetic leakage. Hence it consists of two purely inductive coils wound on a loss free core.

∅

V1

V2

E1

E2

V1

E1

E2

Iμ

∅

V1

V2

E1

E2

V1

E1

E2

Iμ

Let’s consider ideal transformer above, whose secondary is open and primary connected to a sinusoidal voltage V1. This potential difference causes an alternating current to flow in the primary. Since the primary coil is purely inductive and there is no output because the secondary is open, the primary draws magnetizing current Iμ only.

The function of this current is to magnetize the core and it is small and lags  V1 by 90o.

The alternating current Iμ produces alternating flux ∅ which is at all times proportional to Iμ and in phase with it.

The changing flux is linked with both the primary and the secondary windings. Therefore it produces self-induced emf, E1, in the primary. E1 is at every instant equal to and in opposition to  V1. It is also known as counter emf or back emf of the primary.

Similarly, there is produced in the secondary an induced emf, E2, which is known as mutually induced emf. This emf is anti-phase with  V1and its magnitude is proportional to the rate of change of flux and the number of secondary turns.

EMF Equation of a transformer

∅m

∅

t

14f

T=1f

∅m

∅

t

14f

T=1f

Let:

N1=Number of turns in the primary

N2=Number of turns in the secondary

∅m=maximum flux in the core in Webers=Bm×A

f=frequency of alternating supply in Hertz

Flux increases from its zero value to maximum value ∅m in one quarter of the cycle i.e. 14f seconds.

Therefore average rate of change of flux =∅m14f=4f∅m  volts.

Therefore induced voltage per turn =4f∅m  volts.

If the flux ∅ variation is sinusoidal, then the rms value of induced voltage is obtained by multiplying the average value with the form factor.

Form factor=rms valueaverage value=1.11

∴  rms valueemfturn=1.11×4f∅m=4.44f∅m volts

Now rms value of the induced emf in the whole primary winding is:

=(induced emf per turn ×number of primary turns

=4.44fN1∅m   volts

=4.44fN1BmA  volts

Similarly rms value of emf induced in the secondary is:

=(induced emf per turn ×number of secondary turns

=4.44fN2∅m   volts

=4.44fN2BmA  volts

It can be seen that:

E1N1=E2N2=4.44f∅m

i.e. emf per turn is the same for both primary and the secondary.

Voltage transformation ratio (k)

We have seen that    E1N1=E2N2

∴ E1N1=E2N2=k

This constant k is known as the voltage transformation ratio.

If N2>N1, the transformer is called a step up transformer.

If N1>N2, the transformer is called a step down transformer.

Also for ideal transformer, input VA= output VA

V1I1=V2I2   or  I2I1=V1V2=1k

Transformer with losses but no magnetic leakage

- Transformer on no load

When transformer is on no load, primary input current is not usually wholly reactive. The primary input current under no load conditions has to supply iron losses in the core (hysteresis and eddy current losses) and very small amount of copper loses in the primary winding there being no copper losses in the secondary because it is open. Hence, the no load primary current Io is not at 90obehind V1 but lags it by an angle ɸ<90o. The no load input power is given by:

wo=V1Iocosɸo

ɸo

v1

IW

Iμ

Io

E1

E2

ɸo

v1

IW

Iμ

Io

E1

E2

cosɸo is the primary power factor under no load. The current Io has two components. The one in phase with V1 is known as the active or working or iron loss component Iw because it supplies the iron loss plus the small quantity of primary copper loss.

Iw=Iocosɸo

The other component is in quadrature with V1 and is known as the magnetizing component Iμ because its function is to sustain the alternating flux in the core. It is wattles.

Iμ=Iosinɸo

Hence:

Io2=Iw2+Iμ2

As Io is very small, no load copper loss is negligibly small which means that no load primary input is practically equal to the iron loss in the transformer.

The no load primary current Io is approximately one percent of full load current.

- Transformer on load

When the secondary is loaded, the secondary current I2 is set up. The magnitude and phase of I2 with respect to V2 is determined by the characteristics of the load. Current I2 is in phase with V2 if the load is purely resistive, lags behind V2 if the load is inductive and leads V2 is the load is capacitive.

ɸo

V1

V2

1

Io

ɸo

V1

V2

1

Io

ɸ2

V1

V2

2

Io

ɸo

I2

ɸ2

V1

V2

2

Io

ɸo

I2

ɸ2

V1

V2

3

I2/

ɸo

I2

ɸ2/

Io

ɸ2

V1

V2

3

I2/

ɸo

I2

ɸ2/

Io

ɸo

V1

V2

4

I1

I2

ɸo

V1

V2

4

I1

I2

The secondary current sets up its own mmf (N2I2) and hence its own flux ɸ2 which is in opposition to the main primary flux ɸo which is due to Io, as shown in fig. (2)

The opposing secondary flux ɸ2 weakens the primary flux ɸo momentarily, hence primary back emf, E1 tends to be reduced. For a moment V1 gains upper hand over E1 and hence causes more current to flow in the primary.

The additional current in the primary I2' is known as load component of primary current. This current is in anti-phase with I2.

The additional primary magnetomotive force N1I2' sets up its own flux ɸ2' which is in opposition to ɸ2 and is equal to it in magnitude as shown in fig.(3).

Hence the two fluxes ɸ2 and ɸ2', cancel each other out. So we find that the magnetic effects of secondary current  I2 are immediately neutralized by additional primary current I2' which is brought into existence exactly the same time as I2. Hence whatever the load conditions, the net flux passing through the core is approximately the same as at no load as shown in fig. (4). An important conclusion is that due to the constancy of the flux at all loads, the core or iron losses are constant under all load conditions.

ɸ2=ɸ2'                ∴   N2I2=N1I2'

I2'=N2N1I2=kI2

The primary current  I1 has two components;  I0 and I2'.

ɸo

v1

I2'

I1

Io

I2

E2

ɸ1

Pure resistive load

ɸo

v1

I2'

I1

Io

I2

E2

ɸ1

Pure resistive load

ɸo

v1

I2'

I1

Io

I2

E2

ɸ1

inductive load

ɸ2

ɸ2

ɸo

v1

I2'

I1

Io

I2

E2

ɸ1

inductive load

ɸ2

ɸ2

- Transformer with winding resistance

An ideal transformer was supposed to possess no resistance, but in an actual transformer, there is always present some resistance of the primary and secondary windings. Due to this resistance there is some voltage drop in the windings.

∴  V2=E2-I2R2

V1=E1+I1R1

v1

I1

Io

I2

E2

I2'

I1R1

v1

I1

Io

I2

E2

I2'

I1R1

Equivalent resistance

R1

R2

R1

R2

R1 is primary winding resistance and R2 is secondary winding resistance both shown externally. The resistance of the two windings can be transferred to any of the two windings. The advantage of concentrating both the resistances in one winding is that it makes calculations very simple and easy because one has to work in one winding only.

The value of R2 in secondary is equivalent to R2k2 in the primary denoted by  R2' i.e. the equivalent of secondary resistance as referred to primary.

The copper loss in secondary is I22R2. This loss is supplied by primary which takes a current I1. Hence if  R2' is equivalent resistance in primary which would have caused the same loss as R2 in secondary, then;

I12R2'=I22R2

R2'=I2I12R2

R2'=R2k2

Similarly, equivalent primary resistance as referred to secondary is:

R1'=k2R1

Hence we have:

Ro1=R1+R2'

Ro1 is equivalent resistance of the transformer as referred to primary.

R1

R2'

Ro1

R1

R2'

Ro1

Ro2=R2+R1'

Ro2 is equivalent resistance of the transformer as referred to secondary.

R2

R1'

Ro2

R2

R1'

Ro2

Magnetic leakage

It has been assumed that all the flux linked with the primary winding also links the secondary winding. In practice this is impossible. It is found however, that all the flux linked with the primary does not link the secondary but part of it i.e. ɸL1 completes its magnetic circuit by passing through the air rather than around the core. This flux is known as primary leakage flux and is proportional to primary ampere turns alone because the secondary turns do not link magnetic circuit of ɸL1. It induces an emf eL1 in primary but not in secondary.

ɸL2

ɸL1

Load

V1

ɸL2

ɸL1

Load

V1

Similarly, secondary ampere turns sets up leakage flux ɸL2 which is linked with the secondary winding alone. It produces emf eL2 in secondary but not in primary.

The effect of the self-induced voltages eL1 and eL2 is equivalent to a small chocker or inductive coil in series with each winding such that the voltage drop in it is equal to that produced by the leakage flux.

Hence a transformer with magnetic leakage is equivalent to an ideal transformer with inductive coils connected in both primary and secondary circuits.

X1=eL1I1

X2=eL2I2

X2

X1

X2

X1

X1 is primary leakage reactance.

X2 is secondary leakage reactance.

Just like for resistance we have:

X2'=X2k2

X1'=k2X1

Xo1=X1+X2'

Xo2=X2+X1'

Transformer with resistance and leakage reactance

X2

X1

R2

R1

Z1

Z2

X2

X1

R2

R1

Z1

Z2

Z1=X12+R12             ;     Z2=X22+R22

Z2'=Z2k2  ;       Z1'=k2Z1 ;    Z01=Z1+Z2'  ;    Z02=Z2+Z1'

Equivalent circuit

Secondary circuit and its equivalent primary values:

E2

R2

X2

V2

ZL

E2'=E1

R2'

X2'

ZL'

V2'=V2k

≡

E2

R2

X2

V2

ZL

E2'=E1

R2'

X2'

ZL'

V2'=V2k

≡

Combining primary and secondary we get:

V1

R1

X1

ZL

R2

X2

Ro

Xo

V1

R1

X1

ZL

R2

X2

Ro

Xo

≡nt

V1

R1

X1

Ro

Xo

E2'=E1

R2'

X2'

ZL'

V1

R1

X1

Ro

Xo

E2'=E1

R2'

X2'

ZL'

A simplification can be done by transferring exciting winding:

V1

R1

X1

Ro

Xo

R2'

X2'

ZL'

V1

R1

X1

Ro

Xo

R2'

X2'

ZL'

V1

R1

X1

Ro

Xo

R2'

X2'

ZL'

R01

X01

V1

R1

X1

Ro

Xo

R2'

X2'

ZL'

R01

X01

If the exciting winding is ignored, then we have:

V1

R01

X01

ZL'

Z01

V1

R01

X01

ZL'

Z01

Open circuit or no load test

A

V

V1

Watt meter

E2=V2

Low

High

A

V

V1

Watt meter

E2=V2

Low

High

The purpose of this test is to determine the no-load loss or core loss and no load Io which is helpful in finding Xo and Ro.

One winding of the transformer, normally the high voltage side, is left open and the other is connected to supply normal voltage and normal frequency.

With normal voltage, normal flux will be set up in the core and normal iron loses will occur. As Iois very small usually 2 to 10% of rated current copper loss is negligible in primary and nil in secondary. Hence wattmeter reading represents the core loss.

W=V1Iocosɸo

cosɸ=WV1Io

Iμ=Iosinɸ

Iw=Iocosɸ

Xo=V1Iμ

Ro=V1Iw

Short circuit test or impedance test

A

V

Low voltage supply

Watt meter

Low

High

A

V

Low voltage supply

Watt meter

Low

High

This is an economical method to determine Z01, X01and R01 or  Z02, X02 and R02.

In this test one of the winding, usually the low-voltage winding is short circuited by a thick conductor. A low voltage usually (5 to 10%) of the normal primary voltage and at normal frequency is applied to primary voltage and increased till full load current flow in both primary and secondary winding.

Since in this test the applied voltage is a small percentage of the normal voltage, the mutual flux ɸ produced is also a small percentage of its normal value. Hence core losses are very small and hence the wattmeter reading represents full load copper losses i.e. I2R for the whole transformer. If Vsc is the voltage required to get rated load current, then:

Z01=VscI1

W=I12R01

R01=WI12

X01=Z012-R012

Why transformer rating is in KVA

Copper loss of a transformer depends on current and iron loss on voltage. Hence, total loss depends on volt-ampere (VA) and not phase angle between voltages and current i.e. it is independent of power factor.

Efficiency of a transformer

The efficiency of a transformer at a particular load and power factor is given by:

Efficiency=outputinput

But transformer being a highly efficient piece of equipment, it has very small loss, hence it is impractical to try to measure its efficiency by measuring input and output. The quantities are nearly of the same size. A better method is to determine the losses and then calculate the efficiency.

Efficiency=outputoutput+losses=outputoutput+copper losses+iron losses

OR:

ꞑ=input-lossesinput

Condition for maximum efficiency

Copper losses=I12R01            or     I22R02

Iron losses=hysteresis loss and eddy current loss

=wh+we=wi

Considering primary side:

Primary input =V1I1cosɸ1

ꞑ=V1I1cosɸ1-lossesV1I1cosɸ1= V1I1cosɸ1-I12R01-wiV1I1cosɸ1

=1-I1R01V1cosɸ1-wiV1I1cosɸ1

Differentiate both sides with respect to I1

dꞑdI1=0-R01V1cosɸ1+wiV1I12cosɸ1

For ꞑ to be maximum dꞑdI1=0. Hence we have:

R01V1cosɸ1=wiV1I12cosɸ1

I12R01=wi

OR:

Copper = Iron losses.